## DMSMatchingTemplateInfo (hidden)
YesNo | TrueFalse | AlarmEventCause | AlarmSeverity | MeasurementType | TagSemantics | DMSType | DiscreteSignalType | AbnormalState | PhaseCode | WindingType | SignalDirection | AnalogSignalType | UnitSymbol | FlowDirection | RemoteUnitType | TimeZone | RedundancyBehaviorType | SOEGroup | ProtocolTypeConitel | ScanTypeConitel | RemotePointType | OperateType | DiscreteInputTypeConitel | SectionConitel | DiscreteOutputDataTypeConitel | CommandTypeConitel | FunctionCodeConitel | AnalogInputTypeConitel | DeadbandDataType | DNP3Scan | TimeSyncMode |  | DNP3ConfirmMode | DNP3ObjectGroup | DNP3InputType | DNP3OutputType | ControlCode | DNP3Variation | DNP3SlaveEvent | DNP3SlaveDiscreteInputDataType | DNP3SlaveClassData | DNP3SlaveAnalogInputDataType | DNP3SlaveCounterDataType | IccpVersion | IccpBlocks | ConnectionRole | ServiceRole | AuthenticationMode | DstsType | IccpScope | IccpDataValueType | IECCounterInterrogationType | IECClockSyncMode | OctetSize | IEC101LinkMode | IEC101ConfirmMode | ModemCallType | ModemCommandType | BaudRate | IECDiscreteType | IECCommandQualifier | CommandState | IECAnalogType | IECRateType | ScanTypeMD3 | DiscreteInputModuleTypeMD3 | DiscreteInputDataTypeMD3 | DiscreteOutputTypeMD3 | DiscreteOutputDataTypeMD3 | CmdTypeMD3 | AnalogInputModuleTypeMD3 | AnalogInputDataTypeMD3 | AnalogOutputTypeMD3 | ModbusByteOrder | ModbusTransmissionMode | ModbusRegisterType | ModbusDiscreteOutputType | ModbusAnalogType | SecurityCodeSeries5 | ScanTypeSeries5 | DiscreteTypeSeries5 | ScanTypeVanComm | DiscreteInputTypeVanComm | DiscreteOutputTypeVanComm | AnalogTypeVanComm | CalculationParamType | InputTriggerType | RemoteUnitType | OperateType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | OperateType | DNP3InputType | RemotePointType | OperateType | RemotePointType | SignalDirection | OperateType | MeasurementType | RemotePointType | OperateType | RemotePointType | OperateType | RemoteUnitType | RemoteUnitType | RemotePointType | IccpDataValueType | RemotePointType | IccpDataValueType | RemotePointType | SignalDirection | IccpDataValueType | MeasurementType | IccpDataValueType | IccpDataValueType | RemoteUnitType | OctetSize | OctetSize | OctetSize | OctetSize | BaudRate | OctetSize | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | RemotePointType | SignalDirection | MeasurementType | IECAnalogType | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | RemoteUnitType | OctetSize | RemoteUnitType | RemotePointType | IECDiscreteType | IECDiscreteType | RemotePointType | IECAnalogType | IECAnalogType | RemotePointType | SignalDirection | IECAnalogType | IECAnalogType | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | RemotePointType | ModbusRegisterType | RemotePointType | SignalDirection | ModbusRegisterType | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | RemotePointType | RemotePointType | RemotePointType | SignalDirection | MeasurementType | CalculationParamType
No | TRUE | ApplicationAlarm | Severidade 16 | Unitless | DoNotOperatorClose | SUBSTATION | Custom | Normal | Unknown | None | Read | Custom | Default | Undirected | RTU | (UTC-12:00) International Date Line West | PrioritizeCostFactor | Group07 | Conitel2025 | Scan | Analog | DirectOperate | SingleBit | SectionA | SingleCoord | TripClose | Trip | TwelveBitSignedMagnitude | Int32 | Class0 | LAN | None | Never | BinaryInput | SingleBit | SingleCoord | Nul | Empty | WithoutTime | BinaryInputPackedFormat | Class1 | Int32WithFlag | Int32WithFlag | Version1996 | Block1 | Outgoing | Client | None | ManualRBE | Vcc | Unknown | CounterRead | SyncOnly | OneOctet | Unbalanced | Sometimes | DialOut | BaudRate | B100 | IECNone | UseDefault | On | IECShortNormalized | IECRateTimestamp | AnalogUnconditional | DigitalInputModuleDCM | SingleBit | RaiseLower | SingleCoord | Trip | AnalogInputModule | TwelveBitSignedMagnitude | AOMType | LittleEndian | TCP | Coil | SingleCoord | Short | LRC8bit | ExceptionScan | SingleCoord | AnalogScan | MomentaryStatus | SingleCoord | Signed | Bool | None | RTU | DirectOperate | Status | Analog | Analog | Read | Discrete | Status | DirectOperate | SingleBit | Analog | DirectOperate | Analog | Read | DirectOperate | Discrete | Status | DirectOperate | Analog | DirectOperate | ControlCenter | ControlCenter | Status | State | Analog | Real | Analog | Read | Real | Discrete | State | Real | RTU | OneOctet | OneOctet | OneOctet | OneOctet | B9600 | OneOctet | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | Analog | Read | Discrete | IECShortNormalized | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | RTU | OneOctet | RTU | Status | IECSingleBit | IECSingleBit | Analog | IECShortNormalized | IECShortNormalized | Analog | Read | IECShortNormalized | IECShortNormalized | Discrete | Status | Analog | Analog | Read | Discrete | Status | Analog | Coil | Analog | Read | Coil | Discrete | Status | Analog | Analog | Read | Discrete | Status | Analog | Analog | Read | Discrete | Bool
Yes | FALSE | DiscreteState | Severidade 15 | Voltage | DoNotOperatorOpen | BAY | SwitchStatus | Abnormal | N | Primary | Write | MeasuredValue | kV | Forward | SubstationControlSystem | (UTC-11:00) Coordinated Universal Time-11 | SwitchOnFirstRTUFailure | Group8F | Baker | SOEScan | Status | SelectWithValue | SingleBitMCDA | SectionB | TwoCoord | RaiseLower | Close | TwelveBitSignedTwoComplement | Int16 | Class0123 | Serial | Diagnostic | Sometimes | BinaryInputEvent | DoubleBit | MultiCoord | PulseOn | Int32 | WithAbsoluteTime | BinaryInputWithFlags | Class2 | Int16WithFlag | Int16WithFlag | Version2000 | Block2 | Incoming | Server | Mace | ManualInterval | Icc | Real | CounterFreezeWithReset | LoadDelay | TwoOctets | Balanced | Always | DialIn | TelephoneNumber | B200 | IECSingleBit | ShortPulse | Off | IECShortScaled | IECRateShortTimestamp | AnalogDeltaScan | DigitalInputModule | MultiBit | POMType | TwoCoord | Close | FloatingPointModule | TwelveBitSignedTwoComplement | InputPointControl | BigEndian | ASCII | DiscreteInput | TwoCoords | UShort | CRC16bit | StatusScan | DoubleCoord | AllStatusScan | MemoryStatus | DoubleCoord | Unsigned | Int | Value | TerminalServer | AutoSelectWithValue |  | Counter | Counter |  |  |  | AutoSelectWithValue | DoubleBit | Counter | AutoSelectWithValue | Counter |  | AutoSelectWithValue |  |  | AutoSelectWithValue | Counter | AutoSelectWithValue | DSTS | DSTS |  | Discrete | Counter | RealQuality | Counter |  | RealQuality |  | Discrete | RealQuality | ModemBank | TwoOctets | TwoOctets | TwoOctets | TwoOctets |  | TwoOctets |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled | Counter |  |  | IECShortScaled |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled |  | TwoOctets |  |  | IECDoubleBit | IECDoubleBit | Counter | IECShortScaled | IECShortScaled | Counter |  | IECShortScaled | IECShortScaled |  |  | Counter | Counter |  |  |  | Counter | HoldingRegister | Counter |  | HoldingRegister |  |  | Counter | Counter |  |  |  | Counter | Counter |  |  | Int
|  | AnalogHigh | Severidade 14 | Current | DoNotAutoClose | BASEVOLTAGE | Local | Auto | C | Secondary | ReadWrite | ControlSetValue | V | Reverse | ControlCenter | (UTC-10:00) Aleutian Islands | SwitchOnAllRTUFailure |  |  |  | Counter | SelectWithoutValue | MultiBit |  | MultiCoord |  | Raise | SixBitUnsigned | Float | ScanTable |  | Type2 | Always | DoubleBinaryInput | MultiCoord |  | PulseOff | Int16 | WithRelativeTime | DoubleBitBinaryInputPackedFormat | Class3 | Int32WithoutFlag | Int32WithoutFlag |  | Block3 |  | Peer | SSL | AutoAll |  | State | CounterFreezeWithoutReset | DelayAcq | ThreeOctets |  | Never |  | Command | B300 | IECDoubleBit | LongPulse |  | IECFloat | IECRate | DigitalCOSTimeTagged |  | MultiBitBCD | DOMType | MultiCoord | Raise | AnalogInputModuleDCM | TwelveBitUnsigned | FloatingPointOP |  | RTU | InputRegister | MultiCoord | Int32 |  | AnalogScan | MultiCoord | MomentaryStatusScan | LatchingStatus | MultiCoord |  | Double | Flags | [8 empty] | DirectNoAck | MultiCoord |  | DirectNoAck |  |  | DirectNoAck |  |  | DirectNoAck |  | DirectNoAck |  |  |  | StateSupp |  | RealQualityTimeTag |  |  | RealQualityTimeTag |  | StateSupp | RealQualityTimeTag | TerminalServer |  |  |  | Undefined |  | Undefined |  | IECStepPosition | IECStepPosition |  | IECFloat |  |  |  | IECFloat |  | IECStepPosition | IECStepPosition |  | IECFloat |  |  |  |  | IECStepPosition | IECStepPosition |  | IECFloat | IECFloat |  |  | IECFloat | IECFloat | [23 empty] | Double
|  | AnalogLow | Severidade 13 | ActivePower | DoNotAutoOpen | NETWORKINFO | OperationCount |  | CN | Tertiary |  | ControlBandwidth | mV |  | IED | (UTC-10:00) Hawaii | CostFactorWithAvailabilityCheck |  |  |  | SmartMeter | AutoSelectWithValue | MultiBitBCD |  |  |  | Lower | TwelveBitUnsigned |  |  |  | Type1 |  | DoubleBinaryInputEvent | MultiCoordBCD |  | LatchOn | Float |  | DoubleBitBinaryInputWithFlags | None | Int16WithoutFlag | Int16WithoutFlag |  | Block4 |  |  |  | AutoReal |  | Discrete | CounterReset |  | Undefined |  |  |  | Delay | B600 | IECStepPosition | Persistent |  | IECShortNormalizedTimestamp |  | DigitalUnconditional |  |  | InputPointControl |  | Lower |  | FloatingPoint |  |  |  | HoldingRegister |  | UInt32 |  | SetpointScan |  | MemoryStatusScan | Multibit | RaiseLower |  | String | Timestamp | [23 empty] | StateQuality |  | RealExtended |  |  | RealExtended |  | StateQuality | RealExtended | [8 empty] | IECBitstring | IECBitstring | [7 empty] | IECBitstring | IECBitstring | [6 empty] | IECBitstring | IECBitstring |  | IECShortNormalizedTimestamp | IECShortNormalizedTimestamp |  |  | IECShortNormalizedTimestamp | IECShortNormalizedTimestamp | [23 empty] | String
|  | AnalogCreep | Severidade 12 | ReactivePower | WarnOnOpen | FAULTINDICATORC | TapPosition |  | B |  |  | ControlDelay | A |  | SmartMeter | (UTC-09:30) Marquesas Islands | [5 empty] | AutoSelectWithoutValue | SingleBitMCDB |  |  |  |  | RemoteStatusByte | [5 empty] | BinaryOutput |  |  | LatchOff | Double |  |  |  | FloatWithFlag |  |  | Block5 |  |  |  | AutoDiscrete |  | StateSupp | [7 empty] | B1200 | IECBitstring |  |  | IECShortScaledTimestamp |  | FloatingPointUnconditional |  |  |  |  | PointOff |  | FifteenBitSignedMagnitude | [5 empty] | Float |  |  |  | LatchingStatusScan |  |  |  | ASignal | AlarmLimit | [23 empty] | DiscreteQuality |  | RealQualityTimeTagExtended |  |  | RealQualityTimeTagExtended |  | DiscreteQuality | RealQualityTimeTagExtended | [8 empty] | IECMultiBit | IECMultiBit | [7 empty] | IECMultiBit | IECMultiBit | [6 empty] | IECMultiBit | IECMultiBit |  | IECShortScaledTimestamp | IECShortScaledTimestamp |  |  | IECShortScaledTimestamp | IECShortScaledTimestamp | [23 empty] | ASignal
|  | AnalogGrowth | Severidade 11 | CosPhi | WarnOnClose | POWERTRC2W | TapIncrement |  | BN |  |  | ControlSubDelay | kA |  | ModemBank | (UTC-09:00) Alaska | [5 empty] | DirectNoAck | SingleBitMCDC | [10 empty] | BinaryOutputEvent |  |  | ClosePulseOn |  |  |  |  | DoubleWithFlag | [6 empty] | AutoState |  | RealQuality | [7 empty] | B2400 | IECMultiBit |  |  | IECFloatTimestamp |  | FloatingPointDelta |  |  |  |  | PointOn |  | FifteenBitSignedTwoComplement | [9 empty] | StatusExceptionScan |  |  |  | DSignal | [24 empty] | StateSuppQuality | [6 empty] | StateSuppQuality | [10 empty] | IECSingleBitTimestamp | [7 empty] | IECSingleBitTimestamp | [7 empty] | IECSingleBitTimestamp | IECSingleBitTimestamp |  | IECFloatTimestamp | IECFloatTimestamp |  |  | IECFloatTimestamp | IECFloatTimestamp | [23 empty] | DSignal
|  | AnalogFlatline | Severidade 10 | Frequency | Predicted | POWERTRC3W | Enabled |  | BC |  |  | ControlLimitHigh | mA |  | DSTS | (UTC-09:00) Coordinated Universal Time-09 | [6 empty] | DoubleBitMCDA | [10 empty] | BinaryCounter |  |  | TripPulseOn | [13 empty] | StateQuality | [7 empty] | B4800 | IECSingleBitTimestamp |  |  | IECShortNormalizedNoQuality |  | FloatingPointCOSTimeTagged |  |  |  |  | SinglePoleOperate |  | FifteenBitUnsigned | [9 empty] | ReadInternalStatus |  |  |  | BoolArray | [24 empty] | StateQualityTimeTag | [6 empty] | StateQualityTimeTag | [10 empty] | IECDoubleBitTimestamp | [7 empty] | IECDoubleBitTimestamp | [7 empty] | IECDoubleBitTimestamp | IECDoubleBitTimestamp |  | IECShortNormalizedNoQuality | IECShortNormalizedNoQuality |  |  | IECShortNormalizedNoQuality | IECShortNormalizedNoQuality | [23 empty] | ASignalArray
|  | AnalogDrop | Severidade 9 | Temperature | Confirmed | SYNCMACHINEC | LoadBonus |  | BCN |  |  | ControlLimitLow | kW |  | TerminalServer | (UTC-08:00) Baja California | [6 empty] | DoubleBitMCDB | [10 empty] | FrozenCounter |  |  | ClosePulseOff | [13 empty] | DiscreteQuality | [7 empty] | B9600 | IECDoubleBitTimestamp |  |  | IECShortNormalizedShortTimestamp | [6 empty] | CustomPayload0 | [11 empty] | ClearInternalStatus |  |  |  | IntArray | [24 empty] | DiscreteQualityTimeTag | [6 empty] | DiscreteQualityTimeTag | [10 empty] | IECStepPositionTimestamp | [7 empty] | IECStepPositionTimestamp | [7 empty] | IECStepPositionTimestamp | IECStepPositionTimestamp | [30 empty] | DSignalArray
|  | AnalogRTN | Severidade 8 | ActiveEnergy | OutOfOrder | CAPACITORC | ReclosingEnabled |  | A |  |  | ControlSlopeReal | MW |  |  | (UTC-08:00) Coordinated Universal Time-08 | [6 empty] | DoubleBitMCDC | [10 empty] | CounterEvent |  |  | TripPulseOff | [13 empty] | StateSuppQuality | [7 empty] | B19200 | IECStepPositionTimestamp |  |  | IECShortScaledShortTimestamp | [6 empty] | CustomPayload1 | [11 empty] | StatusAcknowledge |  |  |  | DoubleArray | [24 empty] | StateSuppQualityTimeTag | [6 empty] | StateSuppQualityTimeTag | [10 empty] | IECBitstringTimestamp | [7 empty] | IECBitstringTimestamp | [7 empty] | IECBitstringTimestamp | IECBitstringTimestamp
|  | TransformerOverload | Severidade 7 | ReactiveEnergy | Malfunctioning | PETERSENCOILC | ControlActiveSetting |  | AN |  |  | ControlSlopeImag | W |  |  | (UTC-08:00) Pacific Time (US & Canada) | [17 empty] | FrozenCounterEvent |  |  | CloseLatchOn | [13 empty] | RealQualityTimeTag | [7 empty] | B38400 | IECBitstringTimestamp |  |  | IECFloatShortTimestamp | [6 empty] | CustomPayload32 | [15 empty] | StringArray | [24 empty] | StateExtended | [6 empty] | StateExtended | [10 empty] | IECMultiBitTimestamp | [7 empty] | IECMultiBitTimestamp | [7 empty] | IECMultiBitTimestamp | IECMultiBitTimestamp
|  | LineOverload | Severidade 6 | ApparentPower | AlarmInhibit | JUMPERC | Refresh |  | AC |  |  | FaultRecorder | kVAr |  |  | (UTC-07:00) Arizona | [17 empty] | AnalogInput |  |  | TripLatchOn | [13 empty] | StateQualityTimeTag | [7 empty] | B56000 | IECMultiBitTimestamp | [25 empty] | ASignalArray | [24 empty] | DiscreteExtended | [6 empty] | DiscreteExtended | [10 empty] | IECSingleBitShortTimestamp | [7 empty] | IECSingleBitShortTimestamp
|  | AnalogReasonability | Severidade 5 | VoltageAngle | AlarmAudioInhibit | DISCONNECTORC | VoltageIndex1 |  | ACN |  |  | WeatherData | MVAr |  |  | (UTC-07:00) La Paz, Mazatlan | [17 empty] | FrozenAnalogInput |  |  | CloseLatchOff | [13 empty] | DiscreteQualityTimeTag | [7 empty] | B64000 | IECSingleBitShortTimestamp | [25 empty] | DSignalArray | [24 empty] | StateSuppExtended | [6 empty] | StateSuppExtended | [10 empty] | IECDoubleBitShortTimestamp | [7 empty] | IECDoubleBitShortTimestamp
|  | SystemAlarm | Severidade 4 | Status | StopProcessing | SECTIONALIZERC | VoltageIndex2 |  | AB |  |  | BellwetherMeter | VAr |  |  | (UTC-07:00) Mountain Time (US & Canada) | [17 empty] | AnalogInputEvent |  |  | TripLatchOff | [13 empty] | StateSuppQualityTimeTag | [8 empty] | IECDoubleBitShortTimestamp | [50 empty] | StateQualityTimeTagExtended | [6 empty] | StateQualityTimeTagExtended | [10 empty] | IECStepPositionShortTimestamp | [7 empty] | IECStepPositionShortTimestamp
|  | DOMAlarm | Severidade 3 | Discrete | PointTest | LOADBREAKERC | LoadFlowEnabled |  | ABN |  |  | RecloseDelay | Hz |  |  | (UTC-07:00) Yukon | [17 empty] | FrozenAnalogInputEvent | [16 empty] | RealExtended | [8 empty] | IECStepPositionShortTimestamp | [50 empty] | DiscreteQualityTimeTagExtended | [6 empty] | DiscreteQualityTimeTagExtended | [10 empty] | IECBitstringShortTimestamp | [7 empty] | IECBitstringShortTimestamp
|  |  | Severidade 2 | SwitchStatus | DOMInhibit | FUSEC | FaultStatus |  | ABC |  |  | FaultCurrentSub | Hz_s |  |  | (UTC-06:00) Central America | [17 empty] | AnalogOutputStatus | [16 empty] | StateExtended | [8 empty] | IECBitstringShortTimestamp | [50 empty] | StateSuppQualityTimeTagExtended | [6 empty] | StateSuppQualityTimeTagExtended | [10 empty] | IECMultiBitShortTimestamp | [7 empty] | IECMultiBitShortTimestamp
|  |  | Severidade 1 | Time |  | BREAKERC | RecloserLockout |  | ABCN |  |  | FaultAngleSub | C |  |  | (UTC-06:00) Central Time (US & Canada) | [17 empty] | AnalogOutputEvent | [16 empty] | DiscreteExtended | [8 empty] | IECMultiBitShortTimestamp
|  |  |  | Humidity |  | CONNODE | FanStatus |  |  |  |  | FaultCurrentTrans | F |  |  | (UTC-06:00) Easter Island | [17 empty] | ClassObjects | [16 empty] | StateSuppExtended
|  |  |  | WindSpeed |  | BUSNODE | OilPumpStatus |  |  |  |  | FaultAngleTrans | kWh |  |  | (UTC-06:00) Guadalajara, Mexico City, Monterrey | [17 empty] | Authentication | [16 empty] | RealQualityTimeTagExtended
|  |  |  | FeelsLike |  | POTENTIALTR | HotLineTag |  |  |  |  | DeltaVoltage | MWh |  |  | (UTC-06:00) Saskatchewan | [17 empty] | SecureDNP3Statistics | [16 empty] | StateQualityTimeTagExtended
|  |  |  | SunshineMinutes |  | SURGEPROTECTOR | MaxOpCount |  |  |  |  | MaxRampUp | kVArh |  |  | (UTC-05:00) Bogota, Lima, Quito, Rio Branco | [17 empty] | SecureDNP3StatisticsEvent | [16 empty] | DiscreteQualityTimeTagExtended
|  |  |  | SkyCover |  | GNDIMPEDANCE | HourlyOpCount |  |  |  |  | MaxRampDown | MVArh |  |  | (UTC-05:00) Chetumal | [34 empty] | StateSuppQualityTimeTagExtended
|  |  |  | Length |  | CONSUMER | DailyOpCount |  |  |  |  | Charged | kVA |  |  | (UTC-05:00) Eastern Time (US & Canada)
|  |  |  | CrossSection |  | SOURCE | MonthlyOpCount |  |  |  |  | EnergyPrice | MVA |  |  | (UTC-05:00) Haiti
|  |  |  | Impedance |  | CAPACITOR | UnderFrequencyAlarm |  |  |  |  | GenerationPrice | VA |  |  | (UTC-05:00) Havana
|  |  |  | Admittance |  | SYNCMACHINE | Forward |  |  |  |  | PInjectedReal | deg |  |  | (UTC-05:00) Indiana (East)
|  |  |  | ImpedancePerLength |  | CURRENTTR | RelayTrip |  |  |  |  | QInjectedReal | dms |  |  | (UTC-05:00) Turks and Caicos
|  |  |  | AdmittancePerLength |  | INDUCTOR | ReverseMode |  |  |  |  | PInjectedEq | sec |  |  | (UTC-04:00) Atlantic Time (Canada)
|  |  |  | Percent |  | FAULTINDICATOR | SourceStatus |  |  |  |  | QInjectedEq | min |  |  | (UTC-04:00) Caracas
|  |  |  | Money |  | SECTION | Parallel |  |  |  |  | CalculatedVoltage | hour |  |  | (UTC-04:00) Cuiaba
|  |  |  | RelativeVoltage |  | TAPCHANGER | PowerOn |  |  |  |  | PMin | km_h |  |  | (UTC-04:00) Georgetown, La Paz, Manaus, San Juan
|  |  |  | Insolation |  | POWERTR2W | Manageable |  |  |  |  | PMax | mph |  |  | (UTC-04:00) Santiago
|  |  |  | CurrentAngle |  | POWERTR3W | Malfunctioning |  |  |  |  | QMin | m_s |  |  | (UTC-03:30) Newfoundland
|  |  |  | RotationSpeed |  | ASIGNAL | WeightingFactor |  |  |  |  | QMax | m |  |  | (UTC-03:00) Araguaina
|  |  |  | Mass |  | DSIGNAL | TemporaryFault |  |  |  |  | SShortCircuit | km |  |  | (UTC-03:00) Asuncion
|  |  |  | FailureRate |  | GROUNDNODE | GroupStatus |  |  |  |  | X1R1Ratio | ft |  |  | (UTC-03:00) Brasilia
|  |  |  | SoilTemperature |  | REMOTEPOINT | Custom1 |  |  |  |  | RWard | yd |  |  | (UTC-03:00) Cayenne, Fortaleza
|  |  |  | OilTemperature |  | CURVE | Custom2 |  |  |  |  | XWard | mi |  |  | (UTC-03:00) City of Buenos Aires
|  |  |  | HotSpotTemperature |  | PETERSENCOIL | Custom3 |  |  |  |  | R1ShortCircuit | mm2 |  |  | (UTC-03:00) Montevideo
|  |  |  | AbsoluteDateTime |  | COMPSWITCH | Custom4 |  |  |  |  | X1ShortCircuit | kcmil |  |  | (UTC-03:00) Punta Arenas
|  |  |  | LatLong |  | PCELL | Custom5 |  |  |  |  | R2ShortCircuit | AWG |  |  | (UTC-03:00) Saint Pierre and Miquelon
|  |  |  | Date |  | REGCTRL | Custom6 |  |  |  |  | X2ShortCircuit | Ohm |  |  | (UTC-03:00) Salvador
|  |  |  | LongDistanceLength |  | CTRLLIMIT | Custom7 |  |  |  |  | R0ShortCircuit | S |  |  | (UTC-02:00) Coordinated Universal Time-02
|  |  |  | Precipitation |  | DAYTYPE | Custom8 |  |  |  |  | X0ShortCircuit | mS |  |  | (UTC-02:00) Greenland
|  |  |  | WindDirection |  | SEASON | Custom9 |  |  |  |  | Custom1 | uS |  |  | (UTC-02:00) Mid-Atlantic - Old
|  |  |  | ThermalPower |  | LOADRSPCHAR | Custom10 |  |  |  |  | Custom2 | Ohm_km |  |  | (UTC-01:00) Azores
|  |  |  | Emission |  | LOADPICKUPCHAR | [5 empty] | Custom3 | Ohm_m |  |  | (UTC-01:00) Cabo Verde Is.
[6 empty] | LOADGROUP | [5 empty] | Custom4 | Ohm_kft |  |  | (UTC) Coordinated Universal Time
[6 empty] | SECTIONALIZER | [5 empty] | Custom5 | Ohm_mi |  |  | (UTC+00:00) Dublin, Edinburgh, Lisbon, London
[6 empty] | RECLSTAGE | [6 empty] | S_km |  |  | (UTC+00:00) Monrovia, Reykjavik
[6 empty] | PROTECTEQP | [6 empty] | S_m |  |  | (UTC+00:00) Sao Tome
[6 empty] | RELSTAGE | [6 empty] | S_kft |  |  | (UTC+01:00) Casablanca
[6 empty] | RTUC | [6 empty] | S_mi |  |  | (UTC+01:00) Amsterdam, Berlin, Bern, Rome, Stockholm, Vienna
[6 empty] | REGION | [6 empty] | uS_km |  |  | (UTC+01:00) Belgrade, Bratislava, Budapest, Ljubljana, Prague
[6 empty] | SUBREGION | [6 empty] | uS_m |  |  | (UTC+01:00) Brussels, Copenhagen, Madrid, Paris
[6 empty] | FEEDER | [6 empty] | uS_kft |  |  | (UTC+01:00) Sarajevo, Skopje, Warsaw, Zagreb
[6 empty] | FEEDEROBJECT | [6 empty] | uS_mi |  |  | (UTC+01:00) West Central Africa
[6 empty] | ASYNCMACHINE | [6 empty] | Percent |  |  | (UTC+02:00) Athens, Bucharest
[6 empty] | ASYNCMACHINEC | [6 empty] | pu |  |  | (UTC+02:00) Beirut
[6 empty] | WIREC | [6 empty] | base120 |  |  | (UTC+02:00) Cairo
[6 empty] | CABLEC | [6 empty] | currency |  |  | (UTC+02:00) Chisinau
[6 empty] | LINEGEOMETRYC | [6 empty] | W_m2 |  |  | (UTC+02:00) Gaza, Hebron
[6 empty] | WEATHERREGION | [6 empty] | rpm |  |  | (UTC+02:00) Harare, Pretoria
[6 empty] | TRANSFORMERAREA | [6 empty] | kg |  |  | (UTC+02:00) Helsinki, Kyiv, Riga, Sofia, Tallinn, Vilnius
[6 empty] | CONSUMERCONTRACT | [6 empty] | ton |  |  | (UTC+02:00) Jerusalem
[6 empty] | JUMPER | [6 empty] | lb |  |  | (UTC+02:00) Juba
[6 empty] | LOADBREAKSWITCH | [6 empty] | perYear |  |  | (UTC+02:00) Kaliningrad
[6 empty] | BREAKER | [6 empty] | mm_h |  |  | (UTC+02:00) Khartoum
[6 empty] | CBLTHERMMODEL | [6 empty] | in_h |  |  | (UTC+02:00) Tripoli
[6 empty] | ARRAYSIGNAL | [6 empty] | MBTU_h |  |  | (UTC+02:00) Windhoek
[6 empty] | INTERLOCKINGITEM | [6 empty] | kcal_h |  |  | (UTC+03:00) Amman
[6 empty] | INTERLOCKINGSCHEME | [6 empty] | kJ_h |  |  | (UTC+03:00) Baghdad
[6 empty] | CTRLSETT | [6 empty] | MJ_h |  |  | (UTC+03:00) Damascus
[6 empty] | FEEDERSEGMENT | [6 empty] | khour |  |  | (UTC+03:00) Istanbul
[6 empty] | FUSE | [6 empty] | kg_h |  |  | (UTC+03:00) Kuwait, Riyadh
[6 empty] | DISCONNECTOR | [6 empty] | g_h |  |  | (UTC+03:00) Minsk
[6 empty] | TAGC | [9 empty] | (UTC+03:00) Moscow, St. Petersburg
[6 empty] | MOBILEOBJECT | [9 empty] | (UTC+03:00) Nairobi
[6 empty] | AORGROUP | [9 empty] | (UTC+03:00) Volgograd
[6 empty] | CUSTOMGROUP | [9 empty] | (UTC+03:30) Tehran
[6 empty] | INTSCHEDULE | [9 empty] | (UTC+04:00) Abu Dhabi, Muscat
[6 empty] | ANNUALSCHEDULE | [9 empty] | (UTC+04:00) Astrakhan, Ulyanovsk
[6 empty] | LVNETWORK | [9 empty] | (UTC+04:00) Baku
[6 empty] | LVFEEDER | [9 empty] | (UTC+04:00) Izhevsk, Samara
[6 empty] | TEMPSCHEDULE | [9 empty] | (UTC+04:00) Port Louis
[6 empty] | CURRENTTRC | [9 empty] | (UTC+04:00) Saratov
[6 empty] | POTENTIALTRC | [9 empty] | (UTC+04:00) Tbilisi
[6 empty] | MESSAGEMAPPING | [9 empty] | (UTC+04:00) Yerevan
[6 empty] | SEASONDAYSCH | [9 empty] | (UTC+04:30) Kabul
[6 empty] | CUSTOMTYPE | [9 empty] | (UTC+05:00) Ashgabat, Tashkent
[6 empty] | GENCONTRACT | [9 empty] | (UTC+05:00) Astana
[6 empty] | DISTGEN | [9 empty] | (UTC+05:00) Ekaterinburg
[6 empty] | PWRPLANT | [9 empty] | (UTC+05:00) Islamabad, Karachi
[6 empty] | SRVDELIVERYPOINT | [9 empty] | (UTC+05:30) Chennai, Kolkata, Mumbai, New Delhi
[6 empty] | SRVLOCATION | [9 empty] | (UTC+05:30) Sri Jayawardenepura
[6 empty] | BUSBAR | [9 empty] | (UTC+05:45) Kathmandu
[6 empty] | NOTEC | [9 empty] | (UTC+06:00) Bishkek
[6 empty] | DYNAMICLINERATING | [9 empty] | (UTC+06:00) Dhaka
[6 empty] | DYNAMICPWTRATING | [9 empty] | (UTC+06:00) Omsk
[6 empty] | RELSETTS | [9 empty] | (UTC+06:30) Yangon (Rangoon)
[6 empty] | DISTRELSETTS | [9 empty] | (UTC+07:00) Bangkok, Hanoi, Jakarta
[6 empty] | DISTRELSTAGE | [9 empty] | (UTC+07:00) Barnaul, Gorno-Altaysk
[6 empty] | RELCONDITION | [9 empty] | (UTC+07:00) Hovd
[6 empty] | REGCTRLGROUP | [9 empty] | (UTC+07:00) Krasnoyarsk
[6 empty] | TRBANK | [9 empty] | (UTC+07:00) Novosibirsk
[6 empty] | CAPBANK | [9 empty] | (UTC+07:00) Tomsk
[6 empty] | PROTGROUP | [9 empty] | (UTC+08:00) Beijing, Chongqing, Hong Kong, Urumqi
[6 empty] | TRANSMISSION | [9 empty] | (UTC+08:00) Irkutsk
[6 empty] | METERC | [9 empty] | (UTC+08:00) Kuala Lumpur, Singapore
[6 empty] | LOGICALNODE | [9 empty] | (UTC+08:00) Perth
[6 empty] | CUSTOMEQP | [9 empty] | (UTC+08:00) Taipei
[6 empty] | CUSTOMBRANCH | [9 empty] | (UTC+08:00) Ulaanbaatar
[6 empty] | CUSTOMSHUNT | [9 empty] | (UTC+08:45) Eucla
[6 empty] | CUSTOMSWITCH | [9 empty] | (UTC+09:00) Chita
[6 empty] | FLEXIBLELOAD | [9 empty] | (UTC+09:00) Osaka, Sapporo, Tokyo
[6 empty] | LIMITSET | [9 empty] | (UTC+09:00) Pyongyang
[6 empty] | ALARMEVENTC | [9 empty] | (UTC+09:00) Seoul
[6 empty] | SIGNALVALUEALARM | [9 empty] | (UTC+09:00) Yakutsk
[6 empty] | ANALOGALARMLIMITS | [9 empty] | (UTC+09:30) Adelaide
[6 empty] | ADVALMLIMITS | [9 empty] | (UTC+09:30) Darwin
[6 empty] | STORAGE | [9 empty] | (UTC+10:00) Brisbane
[6 empty] | METERCMEAS | [9 empty] | (UTC+10:00) Canberra, Melbourne, Sydney
[6 empty] | PHASETAPCHANGER | [9 empty] | (UTC+10:00) Guam, Port Moresby
[6 empty] | SVC | [9 empty] | (UTC+10:00) Hobart
[6 empty] | COUNTERIEC | [9 empty] | (UTC+10:00) Vladivostok
[6 empty] | AINPUTIEC | [9 empty] | (UTC+10:30) Lord Howe Island
[6 empty] | DINPUTIEC | [9 empty] | (UTC+11:00) Bougainville Island
[6 empty] | AOUTPUTIEC | [9 empty] | (UTC+11:00) Chokurdakh
[6 empty] | DOUTPUTIEC | [9 empty] | (UTC+11:00) Magadan
[6 empty] | SUBRTUIEC104 | [9 empty] | (UTC+11:00) Norfolk Island
[6 empty] | RTUIEC104 | [9 empty] | (UTC+11:00) Sakhalin
[6 empty] | COMMLINKIEC104 | [9 empty] | (UTC+11:00) Solomon Is., New Caledonia
[6 empty] | COMMCHANNELIEC104 | [9 empty] | (UTC+12:00) Anadyr, Petropavlovsk-Kamchatsky
[6 empty] | AINPUTDNP3 | [9 empty] | (UTC+12:00) Auckland, Wellington
[6 empty] | DINPUTDNP3 | [9 empty] | (UTC+12:00) Coordinated Universal Time+12
[6 empty] | AOUTPUTDNP3 | [9 empty] | (UTC+12:00) Fiji
[6 empty] | DOUTPUTDNP3 | [9 empty] | (UTC+12:00) Petropavlovsk-Kamchatsky - Old
[6 empty] | RTUDNP3 | [9 empty] | (UTC+12:45) Chatham Islands
[6 empty] | COMMLINKDNP3 | [9 empty] | (UTC+13:00) Coordinated Universal Time+13
[6 empty] | COMMCHANNELDNP3 | [9 empty] | (UTC+13:00) Nuku'alofa
[6 empty] | COUNTERDNP3 | [9 empty] | (UTC+13:00) Samoa
[6 empty] | REMOTEINPUTICCP | [9 empty] | (UTC+14:00) Kiritimati Island
REMOTEOUTPUTICCP
DSTSICCP
RCCICCP
APPREFICCP
ASSOCIATIONICCP
APROCESSING
DERGROUP
TERMINALSERVER
RTUIEC101
COMMLINKIEC101
COMMCHANNELIEC101
SERIALLINK
TCPIPLINK
CALCCONSTARG
CALCSIGNALARG
CALCPARAM
CALCULATION
CALCCODE
AINPUTADMS
DINPUTADMS
AINPUTMODBUS
DINPUTMODBUS
AOUTPUTMODBUS
DOUTPUTMODBUS
RTUMODBUS
COMMLINKMODBUS
COMMCHANNELMODBUS
MODEM
MODEMBANK
MODEMLINK
SCANGROUPDNP3
NETCONFIGICCP
AINPUT2179
DINPUT2179
RPOINT2179
AOUTPUT2179
DOUTPUT2179
RTU2179
COMMLINK2179
COMMCHANNEL2179
SCANGROUP2179
SUBRTU2179
AINPUTCUSTOM1
DINPUTCUSTOM1
AOUTPUTCUSTOM1
DOUTPUTCUSTOM1
COMMCHANNELCUSTOM1
RTUCUSTOM1
COMMLINKCUSTOM1
AINPUTCUSTOM2
DINPUTCUSTOM2
AOUTPUTCUSTOM2
DOUTPUTCUSTOM2
COMMCHANNELCUSTOM2
RTUCUSTOM2
COMMLINKCUSTOM2
AINPUTCUSTOM3
DINPUTCUSTOM3
AOUTPUTCUSTOM3
DOUTPUTCUSTOM3
COMMCHANNELCUSTOM3
RTUCUSTOM3
COMMLINKCUSTOM3
AINPUT61850
DINPUT61850
AOUTPUT61850
DOUTPUT61850
COMMCHANNEL61850
RTU61850
COMMLINK61850
AINPUTDNP3SLAVE
DINPUTDNP3SLAVE
AOUTPUTDNP3SLAVE
DOUTPUTDNP3SLAVE
COMMCHANNELDNP3SLAVE
RTUDNP3SLAVE
COMMLINKDNP3SLAVE
COUNTERDNP3SLAVE
AINPUTS5
DINPUTS5
AOUTPUTS5
DOUTPUTS5
RTUS5
COMMLINKS5
COMMCHANNELS5
SCANGROUPS5
CONDITIONALSCHM
DOMCATALOG
TEMPLATE
AINPUTMETER
DINPUTMETER
RTUVCOM
COMMLINKVCOM
COMMCHANNELVCOM
SCANGROUPVCOM
AINPUTVCOM
AOUTPUTVCOM
DINPUTVCOM
DOUTPUTVCOM
RTUMD3
COMMLINKMD3
COMMCHANNELMD3
SCANGROUPMD3
AINPUTMD3
AOUTPUTMD3
DINPUTMD3
DOUTPUTMD3
RTUCONITEL
COMMLINKCONITEL
COMMCHANNELCONITEL
SCANGROUPCONITEL
AINPUTCONITEL
AOUTPUTCONITEL
DINPUTCONITEL
DOUTPUTCONITEL
SECUREDNP3
TEMPLATEINSTANCE
TMPMOBILEOBJECT
TMPCUT
TMPGENERATOR
TMPGROUNDING
TMPJUMPER
TMPSWITCH
FAULT
TMPLOAD
CHATTERPROCESSING
EVENTSCHEDULE
AINPUTIECSLAVE
DINPUTIECSLAVE
COUNTERIECSLAVE
AOUTPUTIECSLAVE
DOUTPUTIECSLAVE
RTUIECSLAVE
COMMCHANNELIEC101SLAVE
COMMLINKIEC101SLAVE
UDPLINK
TLS

## DNP3_DiscreteSignals
Signal Details | [22 empty] | Remote Points
DSIGNAL | [22 empty] | REMOTEPOINT | [15 empty] | CHATTERPROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | DSIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | DSIGNAL_MAPPING | DSIGNAL_NORMALVALUE | DSIGNAL_DOMCATALOG | MEASUREMENT_PSR | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | DINPUTDNP3_DATATYPE¦DOUTPUTDNP3_INDATATYPE | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | REMOTEOUTPUTDNP3_POLLAFTERCMD | REMOTEOUTPUTDNP3_POLLDELAY | DOUTPUTDNP3_OUTDATATYPE | REMOTEOUTPUTDNP3_OUTCOORDS | DOUTPUTDNP3_CTRLCODES | DOUTPUTDNP3_CMDTIMES | CHATTERPROCESSING_ENABLE | CHATTERPROCESSING_NUMBEROFCHANGES | CHATTERPROCESSING_OSCILLATIONPERIOD | CHATTERPROCESSING_SUPPRESSIONPERIOD
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Side | Direction | Annual Schedule | Message Mapping | Normal Value | DOM Catalog | Remote Unit | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Command Timeout [s] | Commanding Mode | Input Data Type | Input Coordinates | Output Register | Scan After Command | Scan Delay [s] | Output Data Type | Output Coordinates | Control Codes | Command Times [s] | Enable Oscillation Processing | Number of Changes | Oscillation Period [s] | Suppression Period [s]
FWB_AL13_52-13_43TC |  | 43 - CHAVE TELECOMANDO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Local | ABC | None | Read |  | null@null___INCLUIDO@EXCLUIDO___Local_S_TS_SS | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00406 | 20260416 | Status |  |  | SingleBit | 200 | FALSE
FWB_AL13_52-13_AJG2 |  | AJUSTE PARA GRUPO 2 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | DESATIVAR@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SV | 2 |  | UTR_FWB_1 |  |  | FWB_DS_00407 | 20260416 | Status | 30 | DirectOperate | SingleBit | 202 | FALSE | FALSE | 15 | MultiCoord | 51;52 | ClosePulseOn;ClosePulseOn | 0.25;0.25
FWB_AL13_52-13_SF6A |  | ALARME BAIXA PRESSAO SF6 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00408 | 20260416 | Status |  |  | SingleBit | 206 | FALSE
FWB_AL13_52-13_SF6B |  | BLOQUEIO BAIXA PRESSAO SF6 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00409 | 20260416 | Status |  |  | SingleBit | 207 | FALSE
FWB_AL13_52-13_MOLA |  | MOLA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___CARREGADA@DESCARREGADA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00410 | 20260416 | Status |  |  | SingleBit | 208 | FALSE
FWB_AL13_52-13_CAFL |  | FALTA VCA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 |  |  | FWB_DS_00411 | 20260416 | Status |  |  | SingleBit | 209 | FALSE
FWB_AL13_52-13_CCCO |  | FALTA VCC COMANDO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00412 | 20260416 | Status |  |  | SingleBit | 210 | FALSE
FWB_AL13_52-13_CCMO |  | FALTA VCC MOTOR |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00413 | 20260416 | Status |  |  | SingleBit | 211 | FALSE
FWB_AL13_52-13_CCAB |  | FALTA VCC CIRCUITO ABERTURA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00414 | 20260416 | Status |  |  | SingleBit | 212 | FALSE
FWB_AL13_52-13_43LR |  | 43 - CHAVE LOCAL REMOTO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___REMOTO@LOCAL___Custom_S_TS_SS | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00415 | 20260416 | Status |  |  | SingleBit | 213 | FALSE
FWB_AL13_52-13_BBFC |  | BOBINA FECHAMENTO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00416 | 20260416 | Status |  |  | SingleBit | 214 | FALSE
FWB_AL13_52-13_BBAB |  | BOBINA ABERTURA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SI | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00417 | 20260416 | Status |  |  | SingleBit | 215 | FALSE
FWB_AL13_52-13_CCFL |  | FALTA VCC |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALTA___Custom_S_TS_SB | 2 |  | UTR_FWB_1 |  |  | FWB_DS_00418 | 20260416 | Status |  |  | SingleBit | 216 | FALSE
FWB_AL13_52-13_79 |  | 79 - FUNCAO RELIGAMENTO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | ReclosingEnabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___ReclosingEnabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 |  |  | FWB_DS_00419 | 20260416 | Status | 30 | DirectOperate | SingleBit | 217 | FALSE | FALSE | 15 | SingleCoord | 42;42 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL13_52-13_2649 |  | 26 49 - FUNCAO TEMPERATURA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled_S_TC_SS | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00420 | 20260416 | Status | 30 | DirectOperate | SingleBit | 218 | FALSE | FALSE | 15 | SingleCoord | 44;44 | ClosePulseOn;TripPulseOn | 0.25;0.25
FWB_AL13_52-13_51N |  | 51N |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_51N |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 |  |  | FWB_DS_00421 | 20260416 | Status | 30 | DirectOperate | SingleBit | 219 | FALSE | FALSE | 15 | SingleCoord | 43;43 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL13_52-13_81U1 |  | AJUSTE PARA 81 E1 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00422 | 20260416 | Status | 30 | DirectOperate | SingleBit | 220 | FALSE | FALSE | 5 | SingleCoord | 45 | ClosePulseOn | 0.25
FWB_AL13_52-13_81U2 |  | AJUSTE PARA 81 E2 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00423 | 20260416 | Status | 30 | DirectOperate | SingleBit | 221 | FALSE | FALSE | 5 | SingleCoord | 46 | ClosePulseOn | 0.25
FWB_AL13_52-13_81U3 |  | AJUSTE PARA 81 E3 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00424 | 20260416 | Status | 30 | DirectOperate | SingleBit | 222 | FALSE | FALSE | 5 | SingleCoord | 47 | ClosePulseOn | 0.25
FWB_AL13_52-13_81U4 |  | AJUSTE PARA 81 E4 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00425 | 20260416 | Status | 30 | DirectOperate | SingleBit | 223 | FALSE | FALSE | 5 | SingleCoord | 48 | ClosePulseOn | 0.25
FWB_AL13_52-13_81U5 |  | AJUSTE PARA 81 E5 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | ReadWrite |  | null@ATIVAR___DESATIVADO@ATIVADO___Custom_S_TC_SS | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00426 | 20260416 | Status | 30 | DirectOperate | SingleBit | 224 | FALSE | FALSE | 5 | SingleCoord | 49 | ClosePulseOn | 0.25
FWB_AL13_52-13_81 |  | 81 - FUNCAO SUB/SOB FREQUENCIA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_81 |  | Enabled | ABC | None | ReadWrite |  | INCLUIR@EXCLUIR___INCLUIDO@EXCLUIDO___Enabled___admsINV_S_TC_SS | 2 |  | UTR_FWB_1 |  |  | FWB_DS_00427 | 20260416 | Status | 30 | DirectOperate | SingleBit | 225 | FALSE | FALSE | 5 | SingleCoord | 50;50 | TripPulseOn;ClosePulseOn | 0.25;0.25
FWB_AL13_52-13_TEXT |  | TRIP EXTERNO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SB | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00428 | 20260416 | Status |  |  | SingleBit | 226 | FALSE
FWB_AL13_52-13_62BF |  | 62 - FALHA DISJUNTOR BLOQUEIO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_62BF |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00429 | 20260416 | Status |  |  | SingleBit | 227 | FALSE
FWB_AL13_52-13_50F |  | 50 - SOBRECORRENTE INSTANTANEA FASE |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_50F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA |  |  | UTR_FWB_1 |  |  | FWB_DS_00430 | 20260416 | Status |  |  | SingleBit | 228 | FALSE
FWB_AL13_52-13_51F |  | 51 - SOBRECORRENTE TEMPORIZADA FASE |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_51F |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00431 | 20260416 | Status |  |  | SingleBit | 229 | FALSE
FWB_AL13_52-13_50N |  | 50 - SOBRECORRENTE INSTANTANEA NEUTRO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_50N |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00432 | 20260416 | Status |  |  | SingleBit | 230 | FALSE
FWB_AL13_52-13_51N1 |  | 51 - SOBRECORRENTE TEMPORIZADA NEUTRO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_51N1 |  | RelayTrip | N | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00433 | 20260416 | Status |  |  | SingleBit | 231 | FALSE
FWB_AL13_52-13_SGFT |  | TRIP SGF |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_SGFT |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00434 | 20260416 | Status |  |  | SingleBit | 232 | FALSE
FWB_AL13_52-13_81SU |  | 81 - TRIP SUB FREQUENCIA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_PROT_81SU |  | RelayTrip | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00435 | 20260416 | Status |  |  | SingleBit | 233 | FALSE
FWB_AL13_52-13_79_1 |  | 79 - PARTIDA RELIGAMENTO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00436 | 20260416 | Status |  |  | SingleBit | 234 | FALSE
FWB_AL13_52-13_79OK |  | 79 - RELIGAMENTO COM SUCESSO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00437 | 20260416 | Status |  |  | SingleBit | 235 | FALSE
FWB_AL13_52-13_79LO |  | 79 - RELIGAMENTO BLOQUEADO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | RecloserLockout | ABC | None | Read |  | null@null___NORMAL@ATUADO___Custom_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00438 | 20260416 | Status |  |  | SingleBit | 236 | FALSE
FWB_AL13_52-13_FSIH |  | FALHA SINCRONISMO HORA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00439 | 20260416 | Status |  |  | SingleBit | 238 | FALSE
FWB_AL13_52-13_FLK1 |  | FALHA LINK 1 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00440 | 20260416 | Status |  |  | SingleBit | 239 | FALSE
FWB_AL13_52-13_FLK2 |  | FALHA LINK 2 |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00441 | 20260416 | Status |  |  | SingleBit | 240 | FALSE
FWB_AL13_52-13_FCOM |  | FALHA COMUNICACAO |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@FALHA___Custom_S_TS_SB | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00442 | 20260416 | Status |  |  | SingleBit | 241 | FALSE
FWB_AL13_52-13_TOED |  | 26 49 - TRIP TEMPERATURA |  | Status | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | Custom | ABC | None | Read |  | null@null___NORMAL@ATUADO___RelayTrip_S_TS_SA | 1 |  | UTR_FWB_1 |  |  | FWB_DS_00443 | 20260416 | Status |  |  | SingleBit | 242 | FALSE
FWB_AL13_52-13_DJF1 |  | DISJUNTOR NF |  | SwitchStatus | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | SwitchStatus | ABC | None | ReadWrite |  | DESLIGAR@LIGAR___DESLIGADO@LIGADO___SwitchStatus_D_TC_SE | 2 |  | UTR_FWB_1 |  |  | FWB_DS_00444 | 20260416 | Status | 30 | DirectOperate | MultiCoord | 3;4 | FALSE | FALSE | 15 | SingleCoord | 41;41 | TripPulseOn;ClosePulseOn | 0.25;0.25
Note on A4: Free-text human-readable name of the object. It may be non unique and may not correlate to a naming hierarchy.
Note on B4: If set to Yes, both signal and remote point is going to be deleted from SCADA database upon telemetry data import. If set to No or left empty this column has no impact on telemetry data import process.
Note on C4: Optional string describing an alternate name of the object.
Note on D4: A project-specific unique ID, typically used as an identifier in the external data source system.
Note on E4: Type of the measured quantity, and implied unit (A, kV, kW, Hz...)
Note on F4: An atomic Area of Responsibility (AOR Group) to which this resource belongs
Note on G4: Substation name used as a reference for signal mapping.
Note on H4: Feeder name used as a reference for signal mapping.
Note on I4: Feeder object name used as a reference for signal mapping.
Note on J4: Bank name used as a reference for signal mapping.
Note on K4: Bay name used as a reference for signal mapping.
Note on L4: Device name used as a reference for signal mapping.
Note on M4: Unique ID of the device to which signal is mapped.
Note on N4: Optional field for additional description (not included in telemetry data import).
Note on O4: Meaning of this signal, e.g. "Tap position" or "Switch status"
Note on P4: Measured phases, Unknown if not available/applicable
Note on Q4: Winding of a transformer, or terminal of a conducting equipment (such as switch) where the measurement is located. Except for transformers, may be left unspecified (none).
Note on R4: Specifies if the value can be commanded (written), measured (read), or both.
Note on S4: A signal value (typically non-SCADA controlled) may be scheduled. Examples include public lights, capacitors, and regulating control settings that vary over time.
Note on T4: Describes properties of each possible discrete signal value.
Note on U4: Normal value of this signal. This value is used to initialize the dynamic model during "cold start" of the ADMS.
Note on V4: Specifies properties of device operations monitoring (DOM) performed on this signal.
Note on W4: Physical device or other model resource being measured or controlled
Note on X4: Free-text human-readable name of the object. It may be non unique and may not correlate to a naming hierarchy.
Note on Y4: If set to Yes, remote point is going to be deleted from SCADA database upon telemetry data import. If set to No or left empty this column has no impact on telemetry data import process.
Note on Z4: A project-specific unique ID, typically used as an identifier in the external data source system.
Note on AA4: Optional string describing an alternate name of the object.
Note on AB4: Specifies the kind of the value being transferred: analog (real), discrete (integer), or rate
Note on AC4: timeout for command failure detection
Note on AD4: Type of select-before-operate mechanism used to command the device.
Note on AE4: Specifies if the point value is single-bit (two-state), double-bit (four-state) or complex data type using multiple coordinates.
Note on AF4: Input coordinate(s) on the RTU.
Note on AG4: If true, input point is used to report status of discrete or analog output point.
Note on AH4: Indicates whether scan will be automatically executed after every operate command
Note on AI4: Delay in seconds [s] to begin scan after commanded or un-commanded change.
Note on AJ4: Specifies if the output point is single-coordinate or multi-coordinate (two or more).
Note on AK4: Output coordinate(s) on the RTU.
Note on AL4: Binary command control code corresponding to every possible command (at least two).
Note on AM4: Duration of period during which the output drive remains active, for every possible. Zero indicates that the device uses its pre-configured value.
Note on AN4: Enable oscillation processing.
Note on AO4: Number of status changes required to detect chattering.
Note on AP4: Maximum time interval required to detect chattering.
Note on AQ4: Duration of suppression period. Idle time before oscillation processing is re-applied.

## DNP3_AnalogSignals
Signal Details | [35 empty] | Remote Points
ASIGNAL | [26 empty] | ADVALMLIMITS | [8 empty] | REMOTEPOINT | [17 empty] | APROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | ASIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_UNIT | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | ASIGNAL_FLOWDIRECTION | ASIGNAL_RATEDVALUE | ASIGNAL_MINSETPOINT | ASIGNAL_MAXSETPOINT | ASIGNAL_TRUST | ASIGNAL_ALARMLIMITS | MEASUREMENT_PSR | IDOBJ_NAME | ADVALMLIMITS_ROCALARMGROWTH | ADVALMLIMITS_ROCLIMITGROWTH | ADVALMLIMITS_ROCALARMDROP | ADVALMLIMITS_ROCLIMITDROP | ADVALMLIMITS_FLATLINEALARM | ADVALMLIMITS_FLATLINETIMEOUT | ADVALMLIMITS_CREEPALARM | ADVALMLIMITS_CREEPDEADBAND | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEPOINT_SCALING | REMOTEPOINT_INTERCEPT | REMOTEPOINT_ADCFAIL | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | REMOTEOUTPUT_SPTOL | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | AOUTPUTDNP3_OUTTYPE | REMOTEOUTPUTDNP3_OUTCOORDS | COUNTERDNP3_ENABLEROLLOVER | COUNTERDNP3_ROLLOVER | COUNTERDNP3_RESET | APROCESSING_LOCALDBCHECK | APROCESSING_USERELATIVEDB | APROCESSING_DEADBANDTYPE | APROCESSING_DEADBAND | APROCESSING_ZEROCLAMPINGDB | APROCESSING_LINEARFILTER | APROCESSING_LFFACTOR
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Display Unit | Side | Direction | Annual Schedule | Flow Direction | Rated Value | Min. Setpoint | Max. Setpoint | Trust Factor | Alarm Limits | Remote Unit | Advanced Alarms - Name | Advanced Alarms - Rate-Of-Growth Alarm | Advanced Alarms - Rate-Of-Growth Limit | Advanced Alarms - Rate-Of-Drop Alarm | Advanced Alarms - Rate-Of-Drop Limit | Advanced Alarm - Flatline Alarm | Advanced Alarm - Flatline Timeout [s] | Advanced Alarm - Creep Alarm | Advanced Alarm - Creep Deadband | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Scaling Factor | Intercept | ADC Fail | Command Timeout [s] | Commanding Mode | Setpoint Tolerance | Input Coordinates | Output Register | Output Data Type | Output Coordinates | Enable Rollover | Rollover Value | With Reset | Advanced Processing - Local Deadband Check | Advanced Processing - Use Relative Deadband | Deadband Type | Advanced Processing - Deadband | Advanced Processing - Zero Clamping Deadband | Advanced Processing - Apply Linear Filter | Advanced Processing - Linear Filter Factor
FWB_AL13_52-13_IA |  | IA |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00062 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 41 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IB |  | IB |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | B | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00063 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 42 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IC |  | IC |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | C | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00064 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 43 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IN |  | IN |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | N | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00065 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 44 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_VAB |  | VAB |  | Voltage | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | AB | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 | V_24.2@23.9_21.9@21.6_Trans | UTR_FWB_1 | [11 empty] | FWB_AS_00066 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 45 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_VBC |  | VBC |  | Voltage | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | BC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [11 empty] | FWB_AS_00067 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 46 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_VCA |  | VCA |  | Voltage | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | AC | kV | None | Read |  | Undirected | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [11 empty] | FWB_AS_00068 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 47 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_P |  | P |  | ActivePower | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | ABC | MW | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [11 empty] | FWB_AS_00069 | 20260416 | Analog | 1000 | 0 | FALSE |  |  |  | 48 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_Q |  | Q |  | ReactivePower | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | ABC | MVAr | None | Read |  | Forward | 0 | 0 | 100 | -1 |  | UTR_FWB_1 | [11 empty] | FWB_AS_00070 | 20260416 | Analog | 1000 | 0 | FALSE |  |  |  | 49 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IACC |  | IA DESARME |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | AB | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00071 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 50 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_IBCC |  | IB DESARME |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | BC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00072 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 51 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_ICCC |  | IC DESARME |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | AC | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00073 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 52 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
FWB_AL13_52-13_INCC |  | IN DESARME |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | ABCN | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00074 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 53 | FALSE | [5 empty] | FALSE | FALSE | Float | 0 | 0 | FALSE | 0
Note on A4: Free-text human-readable name of the object. It may be non unique and may not correlate to a naming hierarchy.
Note on B4: If set to Yes, both signal and remote point is going to be deleted from SCADA database upon telemetry data import. If set to No or left empty this column has no impact on telemetry data import process.
Note on C4: Optional string describing an alternate name of the object.
Note on D4: A project-specific unique ID, typically used as an identifier in the external data source system.
Note on E4: Type of the measured quantity, and implied unit (A, kV, kW, Hz...)
Note on F4: An atomic Area of Responsibility (AOR Group) to which this resource belongs
Note on G4: Substation name used as a reference for signal mapping.
Note on H4: Feeder name used as a reference for signal mapping.
Note on I4: Feeder object name used as a reference for signal mapping.
Note on J4: Bank name used as a reference for signal mapping.
Note on K4: Bay name used as a reference for signal mapping.
Note on L4: Device name used as a reference for signal mapping.
Note on M4: Unique ID of the device to which signal is mapped.
Note on N4: Optional field for additional description (not included in telemetry data import).
Note on O4: Meaning of this signal, e.g. "Set point" or "Measured value"
Note on P4: Measured phases, Unknown if not available/applicable
Note on Q4: Engineering unit in which the value is displayed to the operator.
Note on R4: Winding of a transformer, or terminal of a conducting equipment (such as switch) where the measurement is located. Except for transformers, may be left unspecified (none).
Note on S4: Specifies if the value can be commanded (written), measured (read), or both.
Note on T4: A signal value (typically non-SCADA controlled) may be scheduled. Examples include public lights, capacitors, and regulating control settings that vary over time.
Note on U4: Specifies the referent direction of the measurement (typically active power). "Forward" means that the positive sign is when the power flows from the 1st terminal to the second, "Reverse" in the opposite direction, while "Undirected" means that the direction is unspecified.
Note on V4: Rated value (expected maximum) of the signal.
Note on W4: Minimum allowed setpoint (commanded value).
Note on X4: Maximum allowed setpoint (commanded value).
Note on Y4: Value of trust factor for this specific measurement. If -1, the default trust factor for measurements is used; otherwise, that value is overridden.
Note on Z4: Alarm limits applicable to this signal. If absent, no alarms and violations are reported.
Note on AA4: Physical device or other model resource being measured or controlled
Note on AB4: Free-text human-readable name of the object. It may be non unique and may not correlate to a naming hierarchy.
Note on AC4: Alarm raised when the value grows from the previous reading at a rate higher than the specified.
Note on AD4: Rate of variable growth [unit/second] at which a rate-of-growth alarm is raised.
Note on AE4: Alarm raised when the value drops from the previous reading at a rate higher than the specified.
Note on AF4: The rate of value drop [unit/second] at which a rate-of-change alarm appears.
Note on AG4: A flatline alarm is generated if the value change does not exceed the specified limit within a specified time period (timeout).
Note on AH4: Time period during which the value does not change, and the alarm is raised
Note on AI4: Creep alarm is generated when the value does change for more than the specified amount, compared to the setpoint.
Note on AJ4: Deadband of change after which the creep alarm is raised.
Note on AK4: Free-text human-readable name of the object. It may be non unique and may not correlate to a naming hierarchy.
Note on AL4: If set to Yes, remote point is going to be deleted from SCADA database upon telemetry data import. If set to No or left empty this column has no impact on telemetry data import process.
Note on AM4: A project-specific unique ID, typically used as an identifier in the external data source system.
Note on AN4: Optional string describing an alternate name of the object.
Note on AO4: Specifies the kind of the value being transferred: analog (real), discrete (integer), or rate
Note on AP4: Multiplier applied to analog raw value to obtain engineering unit value. (egu = scaling*raw + intercept).
Note on AQ4: Offset added to analog raw value to obtain engineering unit value. (egu = scaling*raw + intercept)
Note on AR4: If true, signal/remote point is included in analog to digital calibration monitoring of RTU.
Note on AS4: timeout for command failure detection
Note on AT4: Type of select-before-operate mechanism used to command the device.
Note on AU4: Allowed tolerance [eng. units] between command and response values, in order to declare the command successful
Note on AV4: Input coordinate(s) on the RTU.
Note on AW4: If true, input point is used to report status of discrete or analog output point.
Note on AX4: Indicates the data type of output point value which will be sent to the remote unit (outstation).
Note on AY4: Output coordinate(s) on the RTU.
Note on AZ4: If true, rollover value of a counter is included when calculating accumulated value.
Note on BA4: Counter (accumulator) roll over value.
Note on BB4: Counter is reset with each acquisition cycle.
Note on BC4: Deadband processing is performed on the SCADA side rather than on the RTU. If true, Percent is permitted as deadband type along with Int32, Int16 and Float.
Note on BD4: Indicates that the deadband value is expressed in percent (only possible with local deadband check); otherwise, it is expressed in engineering units.
Note on BE4: Deadband data type.
Note on BF4: Value of the deadband, in percent or engineering units. If non-zero, signal value variations from the last processed value within the deadband are ignored.
Note on BG4: When the value magnitude is below this limit, it is interpreted as zero. Used to compensate low-value DC bias for older devices.
Note on BH4: Linear filter processing is performed.
Note on BI4: Constant (k) used for value smoothing in linear filter processing.

## DNP3_DiscreteAnalog
Signal Details | [22 empty] | Remote Points | [12 empty] | Remote Points
DSIGNAL | [22 empty] | REMOTEPOINT |  |  |  | ADVALMLIMITS | [8 empty] | REMOTEPOINT |  |  |  |  | APROCESSING
IDOBJ_NAME | DELETE | IDOBJ_ALIAS | IDOBJ_CUSTOMID | MEASUREMENT_TYPE | IDOBJ_AORGROUP | SIGNAL_DEVICEMAPPING | [7 empty] | DSIGNAL_TYPE | MEASUREMENT_PHASE | MEASUREMENT_SIDE | SIGNAL_DIRECTION | SIGNAL_ANNUALSCH | DSIGNAL_NORMALVALUE | DSIGNAL_MAPPING | DSIGNAL_DOMCATALOG | MEASUREMENT_PSR | IDOBJ_NAME | DELETE | IDOBJ_CUSTOMID | IDOBJ_ALIAS | REMOTEPOINT_TYPE | REMOTEPOINT_SCALING | REMOTEPOINT_INTERCEPT | REMOTEPOINT_ADCFAIL | REMOTEOUTPUT_CMDTIMEOUT | REMOTEOUTPUT_SBOMODE | REMOTEOUTPUT_SPTOL | REMOTEINPUTDNP3_INCOORDS¦REMOTEOUTPUTDNP3_INCOORDS | REMOTEINPUTDNP3_OUTREGISTER¦REMOTEOUTPUTDNP3_OUTREGISTER | AOUTPUTDNP3_OUTTYPE | REMOTEOUTPUTDNP3_OUTCOORDS | COUNTERDNP3_ENABLEROLLOVER | COUNTERDNP3_ROLLOVER | COUNTERDNP3_RESET | APROCESSING_LOCALDBCHECK | APROCESSING_USERELATIVEDB | APROCESSING_DEADBANDTYPE | APROCESSING_DEADBAND | APROCESSING_ZEROCLAMPINGDB | APROCESSING_LINEARFILTER | APROCESSING_LFFACTOR
Signal Name | Delete | Signal Alias | Signal Custom ID | Measurement Type | Signal AOR Group | Substation | Feeder | Feeder Object | Bank | Bay | Device | Device Mapping | Description | Signal Type | Phases | Side | Direction | Annual Schedule | Normal Value | Message Mapping | DOM Catalog | Remote Unit | Remote Point Name | Delete Remote Point | Remote Point Custom ID | Remote Point Alias | Remote Point Type | Scaling Factor | Intercept | ADC Fail | Command Timeout [s] | Commanding Mode | Setpoint Tolerance | Input Coordinates | Output Register | Output Data Type | Output Coordinates | Enable Rollover | Rollover Value | With Reset | Advanced Processing - Local Deadband Check | Advanced Processing - Use Relative Deadband | Deadband Type | Advanced Processing - Deadband | Advanced Processing - Zero Clamping Deadband | Advanced Processing - Apply Linear Filter | Advanced Processing - Linear Filter Factor
FWB_AL13_52-13_IA |  | IA |  | Current | SCD Distr | [6 empty] | FWB_AL13_52-13_DJ |  | MeasuredValue | A | A | None | Read |  | Undirected | 0 | 0 | 100 | -1 | I_403.2@null_null@null_Distr | UTR_FWB_1 | [11 empty] | FWB_AS_00062 | 20260416 | Analog | 1 | 0 | FALSE |  |  |  | 41
Note on A4: Free-text human-readable name of the object. It may be non unique and may not correlate to a naming hierarchy.
Note on B4: If set to Yes, both signal and remote point is going to be deleted from SCADA database upon telemetry data import. If set to No or left empty this column has no impact on telemetry data import process.
Note on C4: Optional string describing an alternate name of the object.
Note on D4: A project-specific unique ID, typically used as an identifier in the external data source system.
Note on E4: Type of the measured quantity, and implied unit (A, kV, kW, Hz...)
Note on F4: An atomic Area of Responsibility (AOR Group) to which this resource belongs
Note on G4: Substation name used as a reference for signal mapping.
Note on H4: Feeder name used as a reference for signal mapping.
Note on I4: Feeder object name used as a reference for signal mapping.
Note on J4: Bank name used as a reference for signal mapping.
Note on K4: Bay name used as a reference for signal mapping.
Note on L4: Device name used as a reference for signal mapping.
Note on M4: Unique ID of the device to which signal is mapped.
Note on N4: Optional field for additional description (not included in telemetry data import).
Note on O4: Meaning of this signal, e.g. "Set point" or "Measured value"
Note on P4: Measured phases, Unknown if not available/applicable
Note on Q4: Engineering unit in which the value is displayed to the operator.
Note on R4: Winding of a transformer, or terminal of a conducting equipment (such as switch) where the measurement is located. Except for transformers, may be left unspecified (none).
Note on S4: Specifies if the value can be commanded (written), measured (read), or both.
Note on T4: A signal value (typically non-SCADA controlled) may be scheduled. Examples include public lights, capacitors, and regulating control settings that vary over time.
Note on U4: Specifies the referent direction of the measurement (typically active power). "Forward" means that the positive sign is when the power flows from the 1st terminal to the second, "Reverse" in the opposite direction, while "Undirected" means that the direction is unspecified.
Note on V4: Rated value (expected maximum) of the signal.
Note on W4: Minimum allowed setpoint (commanded value).
Note on X4: Maximum allowed setpoint (commanded value).
Note on Y4: Value of trust factor for this specific measurement. If -1, the default trust factor for measurements is used; otherwise, that value is overridden.
Note on Z4: Alarm limits applicable to this signal. If absent, no alarms and violations are reported.
Note on AA4: Physical device or other model resource being measured or controlled
Note on AB4: Free-text human-readable name of the object. It may be non unique and may not correlate to a naming hierarchy.
Note on AC4: Alarm raised when the value grows from the previous reading at a rate higher than the specified.
Note on AD4: Rate of variable growth [unit/second] at which a rate-of-growth alarm is raised.
Note on AE4: Alarm raised when the value drops from the previous reading at a rate higher than the specified.
Note on AF4: The rate of value drop [unit/second] at which a rate-of-change alarm appears.
Note on AG4: A flatline alarm is generated if the value change does not exceed the specified limit within a specified time period (timeout).
Note on AH4: Time period during which the value does not change, and the alarm is raised
Note on AI4: Creep alarm is generated when the value does change for more than the specified amount, compared to the setpoint.
Note on AJ4: Deadband of change after which the creep alarm is raised.
Note on AK4: Free-text human-readable name of the object. It may be non unique and may not correlate to a naming hierarchy.
Note on AL4: If set to Yes, remote point is going to be deleted from SCADA database upon telemetry data import. If set to No or left empty this column has no impact on telemetry data import process.
Note on AM4: A project-specific unique ID, typically used as an identifier in the external data source system.
Note on AN4: Optional string describing an alternate name of the object.
Note on AO4: Specifies the kind of the value being transferred: analog (real), discrete (integer), or rate
Note on AP4: Multiplier applied to analog raw value to obtain engineering unit value. (egu = scaling*raw + intercept).
Note on AQ4: Offset added to analog raw value to obtain engineering unit value. (egu = scaling*raw + intercept)
Note on AR4: If true, signal/remote point is included in analog to digital calibration monitoring of RTU.
Note on AS4: timeout for command failure detection
Note on AT4: Type of select-before-operate mechanism used to command the device.
Note on AU4: Allowed tolerance [eng. units] between command and response values, in order to declare the command successful
Note on AV4: Input coordinate(s) on the RTU.